Hot Work Procedure

ORG-NTD-000010-SAF-PRC-00099

| Revision History |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Rev | Date | Revision Description | Originator | Reviewer/ Endorser | Approver |
| 0 | 04-15-26 | Issued for Use | HSSE Department | Director, HSSE | VP, Operations |

Change Log

| Revision | Description of Changes and Notes |
| --- | --- |
| 0 | Initial issue. |

Table of Contents

1.0	Purpose	4

2.0	Scope	4

3.0	Roles and Responsibilities	4

4.0	Safety and Health Precautions	4

4.1	Personal Protective Equipment	4

4.2	Chemicals and Hazards	4

4.3	Environmental Requirements	5

5.0	Procedure Title (Enter procedure here.)	5

6.0	Record Keeping Requirements	5

7.0	Training	5

8.0	Sample Styles	6

8.1	Bullets	6

8.2	List Number	6

8.3	Tables	7

8.4	Figures	7

9.0	Definitions	7

9.1	Terms	7

9.2	Abbreviations and Acronyms	8

10.0	References	8

Appendix A.	Example 1	9

Appendix B.	Example 2	10

Purpose

The purpose of this procedure is to establish minimum requirements for the safe planning, authorization, performance, and closure of hot work at NextDecade Corporation and Rio Grande LNG (RGLNG) facilities, and to prevent fire, explosion, and personal injury arising from open-flame or spark-producing activities in or near hydrocarbon process areas.

Scope

This procedure applies to all individuals performing work for or on behalf of NextDecade Corporation, its subsidiary Rio Grande Liquefied Natural Gas (RGLNG), or any other affiliated entity. These entities are collectively referred to as “the company,” and all individuals shall comply with the requirements outlined in this document. These requirements extend to all hot work performed on company property, contractor lay-down areas, marine terminals, the onsite laboratory, or in any other capacity for the company.

Roles and Responsibilities

Roles and responsibilities for this procedure include the following.

| Role | Responsibilities |
| --- | --- |
| Operations Manager (Permit Approver) | Authorize each hot work permit before work begins; deny permits when residual risk is unacceptable. Confirm that adjacent process units are isolated, drained, and gas-free per the Lockout/Tagout Procedure. Suspend hot work and revoke permits if monitoring conditions exceed limits. Review and sign permit close-out at end of shift or end of work. |
| Permit Issuer (Area Supervisor) | Walk down the work site with the Permit Receiver and the Fire Watch before issuing. Verify all preparations: gas testing, area cleared of combustibles within 35 ft, fire-suppression equipment staged. Document all isolations, gas-test readings, and atmospheric monitoring on the permit. Brief the Fire Watch on duties and hand-signals. |
| Permit Receiver (Worker performing the hot work) | Comply with all conditions of the issued permit. Stop work immediately on any change in conditions (gas readings, weather, adjacent operations). Use only inspected hot work equipment with current sticker. Return signed permit to the Issuer at end of work. |
| Fire Watch | Maintain continuous visual line-of-sight on the hot work and the area for the entire duration of work plus 60 minutes after. Operate fire-suppression equipment if needed; sound alarm and evacuate on any indication of fire. Re-test the atmosphere at intervals defined by the permit. No other duties may be performed while serving as Fire Watch. |
| HSSE Advisor | Audit hot work permits in the field; verify atmospheric monitoring and fire-watch coverage. Investigate any near-miss or incident involving hot work; recommend corrective actions. Maintain training records for all personnel authorized to issue, receive, or watch hot work. |

Safety and Health Precautions

Personal Protective Equipment

In all areas except administrative offices, designated parking zones, and the interior of enclosed vehicles, all individuals performing or supervising hot work shall wear the full PPE ensemble: hard hat, safety glasses with side shields, hearing protection appropriate to the task, FR coveralls or FR shirt and FR pants, leather welding gloves, high-cut leather boots, and a welding hood with the appropriate shade lens.

Refer to ORG-NDT-000010-SAF-PRC-00012 — Personal Protective Equipment Procedure — for detailed PPE selection and inspection requirements. Hot work specifically requires that all FR garments be inspected for holes, tears, or contamination prior to each use; damaged garments shall be removed from service.

Hot Work Procedure

Hot work shall be performed only under a current, signed Hot Work Permit. The Permit Receiver completes the steps below in sequence; the Permit Issuer verifies completion of each preparation step before signing the permit; the Fire Watch maintains coverage throughout.

The Permit Receiver and Permit Issuer complete the following:

| Step | Description |
| --- | --- |
| - 1 | Walk down the work area with the Permit Issuer and Fire Watch. Identify all combustibles within a 35-ft radius and either remove them or shield with fire-resistant covers. |
| - 2 | Conduct atmospheric gas testing using a calibrated four-gas monitor. Lower Explosive Limit (LEL) must read 0%. Record reading on the permit. Re-test every 30 minutes during work and after any process change. |
| - 3 | Stage fire-suppression equipment at the work site: minimum two 20-lb ABC dry-chemical extinguishers within arm's reach of the Fire Watch, and one charged 1.5-inch fire hose if working within 50 ft of a process unit. |
| - 4 | Verify that all isolations identified on the permit are in place and tagged. Confirm with the Operations Manager before energizing any hot work equipment. |
| - 5 | Perform the hot work. Stop immediately and re-permit if any of the following change: weather (wind shift, rain), adjacent operations (line break, sample, vent), or atmospheric readings. |
| - 6 | Maintain Fire Watch for 60 minutes after the hot work concludes. Re-inspect for smoldering material; document final inspection on the permit. |
| - 7 | Close out the permit. Permit Receiver signs; Permit Issuer signs; Permit Approver signs. Permit is filed in the Hot Work Permit log. |

Use the following for notes, cautions, and warnings.

|  | Note: The note provides information and clarification to assist with performing the following steps safely and accurately. |
| --- | --- |
|  | Caution: This caution alerts users to potential damage, critical operating limits, and consequences of exceeding those limits, and instructions to follow if limits are exceeded. |
|  | Warning: This alerts users to safety and health hazards and recommends ways to minimize and prevent adverse effects from exposure to hazardous substances and conditions. |

Record Keeping Requirements and Training

Record keeping and training requirements for all NextDecade Corporation and Rio Grande LNG (RGLNG) employees and contractors performing or supervising hot work are detailed in ORG-NTD-000010-HSE-PRC-00037 — Manual — Procedures, Definitions and Record Keeping Requirements. Hot Work Permits and Fire Watch logs shall be retained for a minimum of seven years.

Definitions

Terms

The following terms are specific to this document.

| Term | Definition |
| --- | --- |
| Hot Work | Any work involving an open flame, sparks, heat, or other ignition source, including welding, cutting, brazing, grinding, and thermal lancing. |
| Hot Work Permit | A written, signed authorization that documents preparations, monitoring, and approvals required before hot work may begin. |
| Fire Watch | A trained individual whose sole duty is to observe the hot work area for fire during and after the work, equipped with fire-suppression equipment and authority to stop work. |
| LEL (Lower Explosive Limit) | The minimum concentration of a flammable gas in air below which the mixture is too lean to ignite. Hot work requires 0% LEL at the work area. |

Abbreviations and Acronyms

The following abbreviations and acronyms are specific to this document.

| Abbreviation/Acronym | Definition |
| --- | --- |
| FR | Flame Resistant |
| HSSE | Health, Safety, Security, and Environment |
| LEL | Lower Explosive Limit |
| PPE | Personal Protective Equipment |
| RGLNG | Rio Grande LNG |

References

| Document Number | Document Title |
| --- | --- |
| ORG-NTD-000010-SAF-PRC-00012 | Personal Protective Equipment Procedure |
| ORG-NTD-000010-SAF-PRC-00037 | Lockout/Tagout (LOTO) Procedure |
| ORG-NTD-000010-HSE-PRC-00037 | Manual — Procedures, Definitions and Record Keeping Requirements |
| External | OSHA 29 CFR 1910.252 — Welding, Cutting, and Brazing |
| External | NFPA 51B — Standard for Fire Prevention During Welding, Cutting, and Other Hot Work |

Hot Work Permit Form

The Hot Work Permit Form is maintained electronically in the EHS Permit System. A printed sample is available at the Permit Issuer's station in each control room. The form captures: work description, work location, equipment, isolations, gas-test readings (initial and ongoing), Fire Watch assignment, fire-suppression equipment staged, weather conditions, and signatures of Permit Receiver, Permit Issuer, and Permit Approver.

Fire Watch Checklist

Before assuming Fire Watch duty, the assigned individual confirms: (1) trained and current on Fire Watch responsibilities, (2) line-of-sight on work area is unobstructed, (3) fire-suppression equipment staged and inspected, (4) communication with Permit Receiver established, (5) emergency notification procedure understood. During work: maintain visual contact, monitor atmosphere, take no other duties. After work: continue Fire Watch for 60 minutes, document final inspection, return signed log to Permit Issuer.

| Date: 4/9/2026Error! Use the Home tab to apply DateOnCover to the text that you want to appear here. | Error! Reference source not found. |  |
| --- | --- | --- |
| Rev.: XXXA | 000-NTD-000-xxx-xxx-000xx000-NTD-000-xxx-xxx-000xx |  |

| Date: 4/9/2026Error! Use the Home tab to apply DateOnCover to the text that you want to appear here. | Error! Use the Home tab to apply Title Cover Page to the text that you want to appear here. |  |
| --- | --- | --- |
| Rev.: XXXA | 000-NTD-000-xxx-xxx-000xx |  |