NAME

STANDARD DOCUMENT

xxx-xxx-xxx-xxx-xxx-#####

Table of Contents

A.	INTRODUCTION	3

B.	SCOPE	3

C.	INTEGRATED GOVERNANCE FRAMEWORK	3

D.	DEFINITIONS	3

E.	REFERENCES AND RELATED DOCUMENTS	3

F.	[CONTENT TITLE]	3

G.	[CONTENT TITLE]	3

H.	EXCEPTION REQUEST AND COMPLIANCE AUDITS	4

I.	CONTINUOUS IMPROVEMENT AND REVIEW	4

J.	OWNERSHIP	4

K.	APPROVAL	4

REVISION HISTORY	5

# INTRODUCTION

NextDecade Corporation ("NextDecade" or the "Company") is committed to eliminating fires, explosions, and other loss-of-containment events arising from hot work activities. Compliance with the Hot Work Safety Standard ("Standard") is mandatory.

# SCOPE

This Procedure outlines the step-by-step instructions for authorizing, controlling, executing, and closing out hot work activities at all NextDecade-operated and NextDecade-controlled facilities, including the Rio Grande LNG facility, supporting construction sites, and contractor laydown areas. The Procedure applies to all employees, officers, directors, agents, consultants, contractors, and representatives, and any other individuals when they act on behalf of NextDecade (the "Workforce").

# INTEGRATED GOVERNANCE FRAMEWORK

This Procedure is part of NextDecade's integrated Governance Framework. The Workforce must understand and comply with this Procedure and all other Governance Framework documents applicable to the activity being performed, including the HSSE Standard, the Permit-to-Work Standard, the Lockout/Tagout Procedure, and the Confined Space Entry Procedure where the work occurs in a confined space.

# DEFINITIONS

| - No. | - Term | - Definition |
| --- | --- | --- |
| - 1 | - Hot Work | - Any work that produces a source of ignition — including but not limited to welding, oxy-fuel cutting, plasma cutting, brazing, grinding, soldering, thermal spraying, torch-applied roofing, or any use of open flame or spark-producing equipment. |
| - 2 | - Designated Hot Work Area | - A pre-engineered, fire-safe location specifically constructed or designated for routine hot work, equipped with non-combustible flooring and walls, exhaust ventilation, and posted permit-not-required status. |
| - 3 | - Hot Work Permit | - A written authorization, valid only for a defined location, time window, and scope of work, issued by an authorized Permit Issuer prior to the start of any hot work performed outside a Designated Hot Work Area. |
| - 4 | - Fire Watch | - A trained individual whose sole duty during hot work — and for a continuous post-work period of not less than 30 minutes (60 minutes for elevated risk) — is to detect, suppress, and report fires arising from the hot work activity. |
| - 5 | - Authorized Gas Tester | - A person trained and qualified to operate a calibrated combustible-gas detector and to interpret and record atmospheric readings prior to and during hot work. |

# REFERENCES AND RELATED DOCUMENTS

| - Title | - Document Number |
| --- | --- |
| - NextDecade HSSE Standard | - ND-HSSE-STD-001 |
| - Permit-to-Work Standard | - ND-HSSE-STD-014 |
| - Lockout/Tagout Procedure | - ND-HSSE-PRC-021 |
| - Confined Space Entry Procedure | - ND-HSSE-PRC-022 |
| - NFPA 51B — Standard for Fire Prevention During Welding, Cutting, and Other Hot Work (current edition) | - External |

# PERMIT REQUIREMENTS

A Hot Work Permit is required prior to the start of any hot work activity performed outside a Designated Hot Work Area. The Permit is valid only for the location, time window, scope, and personnel listed on the face of the Permit.

  - The Permit Requester shall complete Sections 1–3 of the Hot Work Permit form (ND-HSSE-FRM-007) and submit the form to the Permit Issuer not less than 24 hours in advance of the planned activity.

  - The Permit Issuer shall conduct a documented job-site walkdown with the Permit Requester and the assigned Fire Watch prior to authorization, verifying that all combustibles within a 35-foot radius have been removed or shielded with approved fire-retardant covers.

  - An Authorized Gas Tester shall record a combustible-gas reading of 0% LEL within the work area and at all openings within 35 feet, immediately prior to permit authorization. Readings shall be re-verified every 60 minutes for the duration of the work.

  - The Permit Issuer shall sign and date the Permit only after verifying that the Fire Watch is in position, equipped with a charged 20-lb ABC extinguisher, and trained in extinguisher use and emergency notification.

  - The Permit shall not exceed one operating shift in duration. Work continuing across shifts requires re-authorization and a re-verified gas test.

# FIRE WATCH RESPONSIBILITIES

The Fire Watch is the single most important control during hot work. The assigned Fire Watch shall remain in continuous attendance throughout the hot work activity and for the post-work fire-watch period defined by the risk classification on the Permit.

  - The Fire Watch shall have no other duties for the duration of the assignment and shall maintain a clear line of sight to the hot work activity at all times.

  - The Fire Watch shall be equipped with, and trained in the use of, a minimum 20-lb ABC fire extinguisher and a charged fire hose where one is reasonably available within 50 feet of the work.

  - The Fire Watch shall halt the work immediately upon observation of smoldering material, smoke, sparks travelling beyond the protected zone, gas-detector alarm, or any other condition that increases fire risk, and shall notify the Permit Issuer.

  - The Fire Watch shall maintain attendance for a minimum of 30 minutes after completion of the hot work, extended to 60 minutes where the work is classified as Elevated Risk on the Permit.

  - Upon close-out, the Fire Watch shall walk down the work area and all adjacent areas where sparks may have travelled, sign Section 6 of the Permit, and return the closed Permit to the Permit Issuer for filing.

# PERMIT SUSPENSION AND EMERGENCY RESPONSE

All hot work activity shall be suspended immediately upon any of the conditions listed below. Resumption of work requires a documented re-authorization by the Permit Issuer.

  - Any combustible-gas detector reading at or above 5% LEL within the work area or within 35 feet of the work.

  - Activation of a facility fire alarm, gas alarm, emergency announcement, or general evacuation order, regardless of source.

  - Loss of the assigned Fire Watch, including absence for any reason exceeding two minutes.

  - Significant change in weather conditions, including sustained wind in excess of 25 mph or electrical storm activity within 10 miles.

  - Discovery of any unaccounted-for combustible material or flammable liquid within the 35-foot radius of the work.

# EXCEPTION REQUEST AND COMPLIANCE AUDITS

When compliance is not feasible or technically possible or when deviation is necessary to support a business function, requests for exceptions to any term or requirement of this Procedure shall be submitted in writing to the Director, HSSE for review. Approved exceptions shall be documented and time-bound, and shall not exceed 30 days without re-authorization.

# CONTINUOUS IMPROVEMENT AND REVIEW

This Procedure will be reviewed at least annually to ensure it remains current and relevant. The Workforce will be informed of any significant revisions in a timely manner. Lessons learned from incidents, near-misses, and audit findings shall be incorporated into subsequent revisions.

# OWNERSHIP

| Responsible | Accountable | Consulted | Informed |
| --- | --- | --- | --- |
| Hot Work Permit Issuer | Director, HSSE | Operations Superintendent; Construction Manager; Fire Watch | All Workforce performing or supporting hot work |

# APPROVAL

| Issuer / Title | Adopted By | Effective / Amended Date |
| --- | --- | --- |
| s/ Director, HSSE | NextDecade Corporation | 14-Apr-2026 |

# REVISION HISTORY

| Revision | Description of Changes and Notes |
| --- | --- |
| 0 | Issued for Use |

The Governance Framework outlines the rules, practices, and processes by which the Company is directed and controlled ensuring accountability, fairness, and transparency in the Company's relationship with its stakeholders, including shareholders, employees, customers, and the community.